## Sheet1
[7 empty] | Data_New |  |  |  | Data_old
[7 empty] | 0.01 CI |  | 0.001 CI |  | 0.01 CI |  | 0.001 CI
| Sensor | Description | Normal range | Operating range | Control points | Remark | low | up | low | up | low | up | low | up
P1 | FIT101 | Flow Transmitter (EMF) | 0-10m3/h | 2.5-2.6m3/h |  | Adjust Manual Valve to Operating Range | 1.5095 | 1.6034 | 1.4965 | 1.6164 | 1.8408 | 1.8491 | 1.8397 | 1.8503
| LIT101 | Level Transmitter (Ultrasonic) | 0-1.2m | 500 - 1100mm | HH=1100mm H=800mm L=500mm LL=250mm | >HH: P601(Permeate Transfer Pump) Cannot Run >H: Close MV-101 <L: Open MV-101 <LL: Stop P-101 & P-102 | 689.0349 | 693.8579 | 688.3656 | 694.5272 | 585.6461 | 586.5516 | 585.5204 | 586.6773
P2 | AIT201 | Analyser (Conductivity) | 0- 1000μS/cm | 30 - 260μS/cm | H=260 μS/cm L=250 μS/cm | >H=Stop P-201 & P-202 <L= Start P-201 & P-202 IF AIT-503 NOT High | 244.3714 | 255.7547 | 242.7916 | 257.3345 | 263.7213 | 263.7567 | 263.7164 | 263.7616
| AIT202 | Analyser (pH) | 2-14 | 6-9 | H=7.05 L=6.95 | >H=Start P-203 & P-204 <L= Stop P-203 & P-204 | 7.7391 | 7.7746 | 7.7342 | 7.7795 | 8.3875 | 8.3882 | 8.3874 | 8.3883
| AIT203 | Analyser (ORP) | 0 - 800mV | 200 - 500mV | H=500mV L=420 mV | >H=Start P-205 & P-206 <L= Stop P-205 & P-206 | 343.6635 | 346.0561 | 343.3315 | 346.3882 | 348.0501 | 348.4113 | 347.9999 | 348.4615
| FIT201 | Flow Transmitter (EMF) | 0-4m3/h | 2.4 - 2.5m3/h | L = 0.5m3/hr | Adjust Manual Valve to Operating Range | 1.5198 | 1.5697 | 1.5129 | 1.5766 | 1.8247 | 1.8324 | 1.8236 | 1.8335
P3 | DPIT301 | DP Transmitter | 0-1 Bar | 0.1 - 0.3 Bar | 0.4 Bar | >0.4 Bar: Activate UF Backwash Cycle | 13.8902 | 14.1965 | 13.8477 | 14.239 | 16.5364 | 16.5858 | 16.5295 | 16.5927
| FIT301 | Flow Transmitter (EMF) | 0-4m3/h | 2.2 - 2.4m3/h | L = 0.5m3/hr | Adjust Manual Valve to Operating Range | 1.5357 | 1.5738 | 1.5304 | 1.5791 | 1.8285 | 1.8345 | 1.8277 | 1.8354
| LIT301 | Level Transmitter (Ultrasonic) | 0-1.2m | 800 - 1000mm | HH=1200mm H=1000mm L=800mm LL=250mm | >HH: Alarm Warning >H: Stop P-101/P-102 <L: Start P-101/P-102 <LL: Stop P-301 & P-302 | 823.631 | 832.8816 | 822.3472 | 834.1654 | 897.1625 | 897.908 | 897.0591 | 898.0115
P4 | AIT401 | Analyser (Hardness) | 0-150 ppm | 5-30ppm | HH=100 H-80 | >HH: Alarm Warning & RO Shutdown Sequence >H: Alarm Warning | 0 | 0 | 0 | 0 | 124.0634 | 124.4671 | 124.0074 | 124.5231
| AIT402 | Analyser | 0-800mV | 150 - 300mV | H=250mV L=240mV | >H: Alarm Warning ==> P-403 & P-404 ON/ STOP P-205 & P-206 <L: STOP P-403 &P-404/ START P-205 & P-206 | 170.8836 | 173.2523 | 170.5549 | 173.5811 | 171.2281 | 171.3224 | 171.215 | 171.3355
| FIT401 | Flow Transmitter (EMF) | 0-4m3/h | 1.5 - 2m3/h | L = 0.5m3/hr | Adjust Manual Valve to Operating Range | 1.4903 | 1.5109 | 1.4874 | 1.5138 | 1.6982 | 1.6992 | 1.6981 | 1.6994
| LIT401 | Level Transmitter (Ultrasonic) | 0-1.2m | 800 - 1000mm | HH=1200mm H=1000mm L=800mm LL=250mm | >HH: Alarm Warning >H: Stop P-301 & P-302 <L: Start P-301 & P-302 <LL: Stop P-401 & P-402 | 814.9861 | 824.1593 | 813.713 | 825.4324 | 880.171 | 880.876 | 880.0732 | 880.9738
P5 | AIT501 | Analyser (pH) | 2-14 | 6-8 | H=8 L=6 | >H: Alarm Warning <L: Alarm Warning | 7.2315 | 7.2437 | 7.2298 | 7.2454 | 7.8706 | 7.8709 | 7.8705 | 7.871
| AIT502 | Analyser (ORP) | 0-800mV | 100-250mV | H=250mV | >H: Alarm Warning/START P-403 & P-404 Shutdown Sequence After 30 mins | 201.0099 | 202.9327 | 200.743 | 203.1995 | 159.287 | 159.385 | 159.2733 | 159.3986
| AIT503 | Analyser (Cond) | 0- 1000μS/cm | 200- 300μS/cm | H = 260μS/cm | >H: Stop P-201 & P202, Overriding AIT 201 | 256.5573 | 256.9533 | 256.5024 | 257.0082 | 266.8489 | 266.8871 | 266.8436 | 266.8924
| AIT504 | Analyser (Cond) | 0-20 μS/cm | 5-10 μS/cm | HH: 15 μS/cm H: 10 μS/cm | >HH: Alarm Warning, ==>Shutdown Sequence After 30 mins >H: Alarm Warning | 37.4343 | 37.6623 | 37.4026 | 37.694 | 12.4193 | 12.4871 | 12.4099 | 12.4965
| FIT501 | Flow Transmitter | 0-4m3/h | 1-2m3/h |  | Design Flow: 1.7m3/h | 1.4994 | 1.5201 | 1.4965 | 1.523 | 1.7081 | 1.7091 | 1.708 | 1.7093
| FIT502 | Flow Transmitter (Paddlewheel) | 0-4m3/h | 1.1 - 1.3m3/h |  | Design Flow: 1.2m3/h | 1.2233 | 1.2402 | 1.2209 | 1.2426 | 1.2676 | 1.2684 | 1.2675 | 1.2685
| FIT503 | Flow Transmitter (EMF) | 0-4m3/hr | 0.7 - 0.9m3/h |  | Design Flow: 0.8m3/h | 0.55084 | 0.55847 | 0.54978 | 0.55953 | 0.73331 | 0.73375 | 0.73325 | 0.73381
| FIT504 | Flow Transmitter (EMF) | 0-2m3/hr | 0.25 - 0.35m3/h |  | Design Flow: 0.3m3/h | 0.28544 | 0.28941 | 0.28489 | 0.28996 | 0.30605 | 0.30623 | 0.30602 | 0.30626
| PIT501 | Pressure Transmitter | 0-5 Bar | 2-3 Bar |  |  | 236.1769 | 239.442 | 235.7237 | 239.8951 | 250.8559 | 250.9999 | 250.8359 | 251.0199
| PIT502 | Pressure Transmitter | 0-5 Bar | 0-0.2 Bar |  |  | 1.3658 | 1.3973 | 1.3614 | 1.4017 | 1.1823 | 1.1839 | 1.1821 | 1.1841
| PIT503 | Pressure Transmitter | 0-5 bar | 1-2 Bar |  |  | 167.106 | 169.311 | 166.8 | 169.6171 | 190.2156 | 190.3273 | 190.2001 | 190.3428
P6 | FIT601 | Flow Transmitter | 0-4m3/h | 2-3m3/h |  |  | 0.013498 | 0.020618 | 0.012509 | 0.021607 | 0.013832 | 0.014919 | 0.013682 | 0.01507

## Sheet2
Data_New |  |  |  | Data_old
0.01 CI |  | 0.001 CI |  | 0.01 CI |  | 0.001 CI
low | up | low | up | low | up | low | up
1.5095 | 1.6034 | 1.4965 | 1.6164 | 1.8408 | 1.8491 | 1.8397 | 1.8503
689.0349 | 693.8579 | 688.3656 | 694.5272 | 585.6461 | 586.5516 | 585.5204 | 586.6773
244.3714 | 255.7547 | 242.7916 | 257.3345 | 263.7213 | 263.7567 | 263.7164 | 263.7616
7.7391 | 7.7746 | 7.7342 | 7.7795 | 8.3875 | 8.3882 | 8.3874 | 8.3883
343.6635 | 346.0561 | 343.3315 | 346.3882 | 348.0501 | 348.4113 | 347.9999 | 348.4615
1.5198 | 1.5697 | 1.5129 | 1.5766 | 1.8247 | 1.8324 | 1.8236 | 1.8335
13.8902 | 14.1965 | 13.8477 | 14.239 | 16.5364 | 16.5858 | 16.5295 | 16.5927
1.5357 | 1.5738 | 1.5304 | 1.5791 | 1.8285 | 1.8345 | 1.8277 | 1.8354
823.631 | 832.8816 | 822.3472 | 834.1654 | 897.1625 | 897.908 | 897.0591 | 898.0115
0 | 0 | 0 | 0 | 124.0634 | 124.4671 | 124.0074 | 124.5231
170.8836 | 173.2523 | 170.5549 | 173.5811 | 171.2281 | 171.3224 | 171.215 | 171.3355
1.4903 | 1.5109 | 1.4874 | 1.5138 | 1.6982 | 1.6992 | 1.6981 | 1.6994
814.9861 | 824.1593 | 813.713 | 825.4324 | 880.171 | 880.876 | 880.0732 | 880.9738
7.2315 | 7.2437 | 7.2298 | 7.2454 | 7.8706 | 7.8709 | 7.8705 | 7.871
201.0099 | 202.9327 | 200.743 | 203.1995 | 159.287 | 159.385 | 159.2733 | 159.3986
256.5573 | 256.9533 | 256.5024 | 257.0082 | 266.8489 | 266.8871 | 266.8436 | 266.8924
37.4343 | 37.6623 | 37.4026 | 37.694 | 12.4193 | 12.4871 | 12.4099 | 12.4965
1.4994 | 1.5201 | 1.4965 | 1.523 | 1.7081 | 1.7091 | 1.708 | 1.7093
1.2233 | 1.2402 | 1.2209 | 1.2426 | 1.2676 | 1.2684 | 1.2675 | 1.2685
0.55084 | 0.55847 | 0.54978 | 0.55953 | 0.73331 | 0.73375 | 0.73325 | 0.73381
0.28544 | 0.28941 | 0.28489 | 0.28996 | 0.30605 | 0.30623 | 0.30602 | 0.30626
236.1769 | 239.442 | 235.7237 | 239.8951 | 250.8559 | 250.9999 | 250.8359 | 251.0199
1.3658 | 1.3973 | 1.3614 | 1.4017 | 1.1823 | 1.1839 | 1.1821 | 1.1841
167.106 | 169.311 | 166.8 | 169.6171 | 190.2156 | 190.3273 | 190.2001 | 190.3428
0.013498 | 0.020618 | 0.012509 | 0.021607 | 0.013832 | 0.014919 | 0.013682 | 0.01507